- GENERAL

** NOTE TO SPECIFIER ** Delete items below not required for project.

1.1	RELATED SECTIONS

.1 23 .. ..

1.2	REFERENCES

.1 ASME – American Society of Mechanical Engineers.

.2 CRN – Canadian Registration Number

.3 ANSI – American National Standards Institute.

.4 ISO – International Standards Organization

1.3	SUBMITTALS

.1 Submit data cover sheet.

.2 Dimensional print(s).

.3 Pressure drop graphs.

.4 Installation & Servicing manual.

1.4	ASSURANCE

.1 The product manufacturer shall be fully certified by the International Organization for Standardization 9001 – Quality Management Systems & ISO 14001 Environmental Management Systems

Part 2 PRODUCTS

2.1	MAGNETIC DIRT FILTERS

.1 Standard of acceptance:  ADEY® MagnaClean® (model Commercial 2”, 3”, 4”, 6” & 8”).

.2 The magnetic filter shall be designed, constructed, and stamped in accordance with Section 	VIII, Division I of the ASME Boiler and Pressure Vessel Code, and registered with the Canadian 	Registration Number.

.3 The magnetic filter shall come with High Power, NdFeB, neodymium magnets in the flow of 	water

.4 The magnetic filter magnets should be individually removeable to facilitate routine cleaning/servicing

.5 The magnetic filter shall be rated for 145 psi (10 bar) maximum working pressure.

.6 The magnetic filter shall have a maximum temperature rating of 212°F (100°C).

.7 The magnetic filter body shall be made of one cast mold 304L stainless steel

.8 The magnetic filter housing, lid & pocket sleeves shall be made of 304L stainless steel 	(SA351CF3)

.9 The magnetic filter shall be supplied with ASME B16.5 Class150 flanges

.10 The magnetic filter shall be supplied with EPDM gaskets

.11 The magnetic filter body shall be at least one and a half times the nominal inlet/outlet pipe diameter

.12 The magnetic filter shall include a threaded blow down connection to allow for magnetite 	and debris to be regularly cleaned out of the unit

.13 The magnetic filter shall include a threaded air removal connection on top of the unit so the 	pressure can be released as part of servicing the unit

.14 Flange end connections should be designed according to ANSI Standards

2.2	ACCESSORIES

.1 Magnetic Dirt Filters Accessories

.1 Thermal Jacket

Part 3 EXECUTION

3.1	INSTALLATION

.1 Install magnetic filter in accordance with manufacturer’s instructions.